## LoadCalcChecklist
Category | Item | Keywords | Required (Y/N) | Notes | Active (Y/N)
HAP Air Conditioning Report | Design Weather Data | Design Weather Data¦Weather Data | Y | Design-day conditions used for the run. Found MISSING on F12-04-233's real HAP export (docs/PROCEDURE.md #21, formalizing an earlier manual review). | Y
HAP Air Conditioning Report | Zone Sizing Summary | Zone Sizing Summary | Y | Present and complete on F12-04-233. | Y
HAP Air Conditioning Report | System Input Data | System Input Data | Y | System-level configuration/assumptions, not just the brief Air System Information block on a DOAS page. Found MISSING on F12-04-233. | Y
HAP Air Conditioning Report | System Output Data / Design Load Summary | System Output Data¦System Design Load Summary¦Design Load Summary | Y | Total system cooling/heating capacity, coil loads, OA/fan data at the system level. Found MISSING on F12-04-233. | Y
HAP Air Conditioning Report | DOAS Sizing Summary | DOAS¦Dedicated Outdoor Air System | Y | Present and complete on F12-04-233. | Y
HAP Air Conditioning Report | Ventilation Sizing Summary | Ventilation Sizing Summary | Y | Present and complete on F12-04-233. | Y
Water Storage Sizing | Tank Capacity Derivation | Water Storage Calculation¦Tank Sizing Calculation¦Storage Capacity Calculation¦Autonomy Days¦Daily Water Demand | Y | F12-04-233's transfer pump calc used "Total Water Capacity to be filled = 4 m3" as a bare input with no calc showing daily demand x storage/autonomy days (or fire reserve). Presence-only check -- cannot verify a found derivation is numerically correct, only that some derivation section/heading appears somewhere in the document. | Y
Pump Duty Calc | Pump Head and Flow | Pump Duty Calculation¦Total Dynamic Head¦Pump Head | Y | Present and complete for all 7 pumps on F12-04-233. | Y
Sump Pit Sizing | Sump Pit and Pump Calc | Sump Pit | Y | Present and complete on F12-04-233. | Y