## VelocityLimits
Type (Duct/Pipe) | System | Min Velocity (m/s) | Max Velocity (m/s) | Code Basis | Notes | Active (Y/N)
Duct | Supply |  | 8 | ASHRAE Fundamentals Ch.21 / SMACNA | Commercial main-duct range per ASHRAE is 5.1-8.0 m/s (1000-1600 fpm) for offices; this table uses the upper bound as a single ceiling since main/branch runs aren't distinguished yet. Branch runs should trend lower for noise even though that isn't separately enforced here. | Y
Duct | Return |  | 4 | ASHRAE Fundamentals Ch.21 | Typical return-duct range is 2.0-4.0 m/s (400-800 fpm); upper bound used as the ceiling. | Y
Duct | Exhaust |  | 8 | ASHRAE Fundamentals Ch.21 (by analogy to Supply) | No distinctly-cited general-exhaust-duct table was found separate from supply air; using the supply ceiling as a placeholder. Kitchen grease/fume-hood exhaust has its own, much higher, code-mandated MINIMUM velocity — that is not this row; use "Other" and confirm per project until a dedicated row is added. | Y
Duct | Fresh/Outside Air |  | 2.5 | ASHRAE Fundamentals Ch.21 (louver guidance) | Governed by weather-louver face velocity, typically capped at 400-500 fpm (2.0-2.5 m/s) to limit moisture/debris carry-through; the ductwork itself could run faster, but the louver is usually the controlling element. | Y
Duct | Other |  |  | -- | No firm-wide default. Project-specific ducts (kitchen exhaust, fume hood, high-velocity systems) need a case-by-case limit set by the senior reviewer before this row is enabled. | N
Pipe | Domestic Cold Water |  | 2.5 | Jordanian National Building Code - Unified Plumbing Code (2013) Section 6.10.12 / ASPE Data Book | Jordanian code Section 6.10.12 states max 2.5 m/s for cold water in copper pipe/fittings and in non-copper pipe using copper-alloy fittings (matches UPC-derived national code text, Codes/plumbing_Code.pdf). Supersedes the prior 2.4 m/s (8 ft/s) ASPE/IPC-sourced ceiling. | Y
Pipe | Domestic Hot Water |  | 1.5 | Jordanian National Building Code - Unified Plumbing Code (2013) Section 6.10.12 / ASPE Data Book | Jordanian code Section 6.10.12 confirms max 1.5 m/s for hot water in copper pipe/fittings and in non-copper pipe using copper-alloy fittings -- matches the prior ASPE/IPC-sourced value exactly (Codes/plumbing_Code.pdf). | Y
Pipe | Drainage (gravity) | 0.6 |  | IPC Table 704.1 / ASCE-WEF MOP FD-5 | 2 ft/s (0.6 m/s) is a MINIMUM self-cleansing velocity at design flow, achieved via slope, not a maximum — gravity drainage has no upper velocity ceiling in this table. | Y
Pipe | Sewage/Sump Force Main | 0.6 | 2.4 | ASPE Data Book (by analogy, not independently sourced) | Min mirrors the same self-cleansing principle as gravity drainage; max mirrors the domestic-cold-water erosion ceiling. Not independently sourced for force mains specifically — confirm before relying on it for a real project. | N
Pipe | Fuel Gas |  |  | ASHRAE Fundamentals Ch.22 / NFPA 54 / IFGC | Building fuel-gas piping is sized to an allowable pressure-drop fraction (typically <10% of inlet pressure), not a fixed velocity ceiling — no numeric limit populated here. Erosional-velocity formulas like API RP 14E's Ve=C/sqrt(rho) are an oil & gas transmission-pipeline standard, not applicable to building fuel-gas piping — do not reuse those numbers here. | N
Pipe | Medical Gas |  |  | NFPA 99 (unconfirmed) | No confirmed numeric velocity limit found in NFPA 99 itself via research. A ~6 m/s (20 ft/s) figure is sometimes cited informally in industry guidance but could not be verified against the standard's text. Confirm with a current NFPA 99 copy before enabling. | N
Pipe | Steam |  | 15 | Spirax Sarco / ASHRAE Fundamentals Ch.22 | 15 m/s is the low-pressure steam guideline; medium-pressure systems can go to ~25 m/s and 40 m/s is cited as a practical upper limit at any pressure before noise/erosion (wet steam) become a problem. This table has one blended "Steam" category (no pressure-class split yet) — uses the conservative low-pressure figure. | Y
Pipe | Fire - Standpipe/Hydrant/Landing Valve/Siamese |  | 6.1 | NFPA 14 | 20 ft/s (6.1 m/s), mandatory. Confirmed via research 2026-09-14 (docs/PROCEDURE.md §14). | Y
Pipe | Fire - Pump Suction |  | 4.6 | NFPA 20 | 15 ft/s (4.6 m/s), for the 10-pipe-diameter run upstream of the fire pump. | Y
Pipe | Fire - Sprinkler/Deluge |  |  | NFPA 13 | No fixed velocity limit — governed by the required hydraulic calculation (minimum pressure/flow at the most remote head), not a velocity ceiling. FM Global's 9.1 m/s (30 ft/s) is a practical sanity-check bound above which Hazen-Williams becomes unreliable, not a real limit — do not enforce it as FAIL. | N
Pipe | Fire - Hose Reel |  |  | BS EN 671 (unconfirmed) | This firm's hose reel/hose rack naming follows British/European convention, not NFPA's (no direct NFPA equivalent for small-bore occupant hose reels). Needs confirming against BS EN 671-1/671-3 before a limit is set. | N