## ManholeSizeLimits
Min Depth (m) | Max Depth (m) | Min Size Round (mm) | Min Size Square (mm) | Code Basis | Notes | Active (Y/N)
0 | 0.6 | 190 | 100 | UK Approved Document H, Table 11 | Inspection chamber, shallow tier, drains <=150mm only. Round min 190mm diameter; rectangular min 225x100mm (100mm = smaller side). Non-Jordanian reference (best practically-searchable stand-in, same convention as VelocityLimits.xlsx/DrainageSlopeLimits.xlsx) -- UK Building Regulations Approved Document H, scoped to domestic/small non-domestic buildings, is the closest fit for private on-site building drainage (not a public sewer). | Y
0.6 | 1.2 | 450 | 450 | UK Approved Document H, Table 11 | Inspection chamber, deeper tier -- min 450mm both round and rectangular (min side). Table 11 Note 3: beyond 1.2m depth the cover opening is deliberately restricted to a max 350mm clear opening to deter entry, formalising the inspection-chamber/manhole split at this depth. | Y
1.2 |  | 1200 | 675 | UK Approved Document H, Table 12 (footnote 7) | Beyond 1.2m depth the chamber is classed as a full manhole, not an inspection chamber -- Table 12 footnote 7 gives 1200mm diameter / 1200x675mm rectangular as the general minimum for any manhole serving a drain (675mm = smaller side used here). KNOWN SIMPLIFICATION: Table 12 itself further reduces this for smaller connecting pipes at depth <1.5m (e.g. 1000mm min for a 150mm pipe) -- this row ignores that refinement and always applies the general 1200/675mm floor, so it is more conservative than the code strictly requires for a small pipe just past 1.2m depth. Also note Approved Document H para 2.54: manholes deeper than 1m should have step irons or a fixed ladder (not numerically enforced by this check). | Y